CONTOSO INDUSTRIAL

# Field Inspection Report

Claim C-2026-04139

| Claim reference | C-2026-04139 |
| --- | --- |
| Serial number | CIE-4000-CH-01400 |
| Product | 4000-series industrial chiller |
| Service partner | Fabrikam Service Partners |
| Date of repair | 2026-06-01 |
| Operation code | HYD-PUMP-RR |
| Running hours at repair | 8,400 |

# Findings

Hydraulic pump seized under load. Drive coupling intact. No external impact damage. Pump removed and replaced.

# Parts fitted

| Part number | Description | Quantity |
| --- | --- | --- |
| P-44120-A | Hydraulic pump assembly, rev A | 1 |

# Labour

5.5 hours claimed against operation HYD-PUMP-RR.

Inspected by: Sunil Bhat, Field Engineer, Fabrikam Service Partners