CONTOSO INDUSTRIAL

# Field Inspection Report

Claim C-2026-04171

| Claim reference | C-2026-04171 |
| --- | --- |
| Serial number | CIE-4000-CH-01960 |
| Product | 4000-series industrial chiller |
| Service partner | Fabrikam Service Partners |
| Date of repair | 2026-05-01 |
| Operation code | CTRL-BD-RR |
| Running hours at repair | 3,000 |

# Findings

Control board unresponsive on power-up. No evidence of moisture ingress or surge damage. Board replaced.

# Parts fitted

| Part number | Description | Quantity |
| --- | --- | --- |
| P-44900 | Control board | 1 |

# Labour

1.5 hours claimed against operation CTRL-BD-RR.

Inspected by: Sunil Bhat, Field Engineer, Fabrikam Service Partners